## Parameters
Refinery Cogeneration MILP — Parameter Sheet
Legend: blue = input value (edit here) · black = formula · Basis column notes grounded vs representative
1. Steam Headers
Parameter | Value | Unit | Basis
HP header pressure | 45 | bar | Grounded — mid-range of 45-60 bar refinery HP practice
MP header pressure | 15 | bar | Grounded — mid-range of 12-17 bar
LP header pressure | 5 | bar | Grounded — mid-range of 4-6 bar
HP steam enthalpy | 2800 | kJ/kg | Grounded — standard steam tables, saturated ~45 bar
MP steam enthalpy | 2790 | kJ/kg | Grounded — standard steam tables, ~15 bar
LP steam enthalpy | 2750 | kJ/kg | Grounded — standard steam tables, ~5 bar
2. Boilers
Parameter | Value | Unit | Basis
Number of boilers | 2 | count | Derived — standard redundancy for mid-size refinery utility
Capacity per boiler | 60 | t/h HP steam | Derived/Scaled — sized with margin over demand profile
Total boiler capacity | 120 | t/h HP steam | Formula = Number of boilers x Capacity per boiler
Min-load (turndown) | 0.3 | fraction of capacity | Grounded — typical industrial boiler turndown limit
Boiler thermal efficiency | 0.85 | fraction | Grounded — standard industrial boiler efficiency (85-90%)
3. Fuel
Parameter | Value | Unit | Basis
Refinery fuel gas (RFG) calorific value | 40 | MJ/kg | Grounded — mid-range of 35-45 MJ/kg from natural-gas-composition data
Purchased natural gas price | 37.5 | Rs/kg | Derived — representative Indian industrial PNG price range (35-40)
Flaring penalty | 5 | Rs/kg RFG flared | Derived — nominal penalty per project plan item 9
4. Turbine / Letdown
Parameter | Value | Unit | Basis
Turbine max capacity | 15 | MW | Derived/Scaled — sized against electricity demand profile
Turbine steam rate (back-pressure) | 8 | kg steam / kWh | Grounded — standard industrial back-pressure turbine range (6-10)
5. Electricity / Tariff (ToD)
Parameter | Value | Unit | Basis
Grid base rate | 4.5 | Rs/kWh | Grounded — IEX day-ahead avg Rs4.88 (Aug'26), Rs3.86 (FY26 avg); 4.5 is a defensible midpoint
ToD peak multiplier (6-10 PM) | 0.2 | fraction above base | Grounded — national ToD rule: peak +10-20%
ToD solar/off-peak discount (10 AM-4 PM) | 0.2 | fraction below base | Grounded — national ToD rule: solar hours -10-20%
Peak rate | 5.4 | Rs/kWh | Formula = base rate x (1 + peak multiplier)
Solar/off-peak rate | 3.6 | Rs/kWh | Formula = base rate x (1 - solar discount)
Normal-hours rate | 4.5 | Rs/kWh | Formula = base rate
6. Electricity Demand
Parameter | Value | Unit | Basis
Plant electricity demand — baseline level | 12 | MW | Derived/Scaled — flat-ish with mild daytime rise
7. Battery
Parameter | Value | Unit | Basis
Battery capacity | 5 | MWh | Derived/Scaled — carried over from existing project
Max charge/discharge rate | 1 | MW | Derived/Scaled
Round-trip efficiency | 0.9 | fraction | Grounded — typical Li-ion round-trip efficiency
End-of-day SOC constraint | Return to start-of-day SOC | - | Carried over from existing model logic
8. Steam Demand Components (representative, not plant-specific)
Parameter | Value | Unit | Basis
HP: CDU baseload | 40 | t/h | Representative — typical CDU steam draw, roughly flat
HP: Hydrocracker baseload | 15 | t/h | Representative — roughly flat
MP: Hydrotreater draw | 20 | t/h | Representative — mild variation with unit campaigns
LP: Tank heating / stripping | 10 | t/h | Representative — slightly higher overnight

## Hourly_Profile
24-Hour Input Vectors
All prices and demand values are formulas referencing Parameters — edit inputs there and this sheet recalculates.
Hour (0-23) | Tariff Band | Electricity Price (Rs/kWh) | HP Steam Demand (t/h) | MP Steam Demand (t/h) | LP Steam Demand (t/h) | Electricity Demand (MW) | RFG Availability (kg/h)
0 | Normal | 4.5 | 55 | 20.8415 | 10.7071 | 11.04 | 1181.8595
1 | Normal | 4.5 | 55.4271 | 20.9526 | 10.866 | 11.0727 | 1154.1214
2 | Normal | 4.5 | 55.825 | 20.9989 | 10.9659 | 11.1686 | 1115.8803
3 | Normal | 4.5 | 56.1667 | 20.9771 | 11 | 11.3212 | 1069.742
4 | Normal | 4.5 | 56.4289 | 20.8887 | 10.9659 | 11.52 | 1018.851
5 | Normal | 4.5 | 56.5938 | 20.7397 | 10.866 | 11.7515 | 966.6753
6 | Normal | 4.5 | 56.65 | 20.5403 | 10.7071 | 12 | 916.7706
7 | Normal | 4.5 | 56.5938 | 20.3041 | 10.5 | 12.2485 | 872.5379
8 | Normal | 4.5 | 56.4289 | 20.0472 | 10.2588 | 12.48 | 836.9915
9 | Normal | 4.5 | 56.1667 | 19.787 | 10 | 12.6788 | 812.5539
10 | Solar/Off-peak | 3.6 | 55.825 | 19.5414 | 9.7412 | 12.8314 | 800.8904
11 | Solar/Off-peak | 3.6 | 55.4271 | 19.327 | 9.5 | 12.9273 | 802.7959
12 | Solar/Off-peak | 3.6 | 55 | 19.1585 | 9.2929 | 12.96 | 818.1405
13 | Solar/Off-peak | 3.6 | 54.5729 | 19.0474 | 9.134 | 12.9273 | 845.8786
14 | Solar/Off-peak | 3.6 | 54.175 | 19.0011 | 9.0341 | 12.8314 | 884.1197
15 | Solar/Off-peak | 3.6 | 53.8333 | 19.0229 | 9 | 12.6788 | 930.258
16 | Normal | 4.5 | 53.5711 | 19.1113 | 9.0341 | 12.48 | 981.149
17 | Normal | 4.5 | 53.4062 | 19.2603 | 9.134 | 12.2485 | 1033.3247
18 | Peak | 5.4 | 53.35 | 19.4597 | 9.2929 | 12 | 1083.2294
19 | Peak | 5.4 | 53.4062 | 19.6959 | 9.5 | 11.7515 | 1127.4621
20 | Peak | 5.4 | 53.5711 | 19.9528 | 9.7412 | 11.52 | 1163.0085
21 | Peak | 5.4 | 53.8333 | 20.213 | 10 | 11.3212 | 1187.4461
22 | Normal | 4.5 | 54.175 | 20.4586 | 10.2588 | 11.1686 | 1199.1096
23 | Normal | 4.5 | 54.5729 | 20.673 | 10.5 | 11.0727 | 1197.2041
Daily avg |  | 4.425 | 55 | 20 | 10 | 12 | 1000

## Notes & Sources
Notes, Assumptions & Sources
Grounded values
Sourced from real industry data: refinery steam header pressure ranges, natural gas/RFG calorific value ranges, Indian ToD tariff structure (national rule: peak +10-20%, solar hours -10-20%), and IEX day-ahead/real-time market clearing prices (Aug 2026 / FY26 averages).
Derived/Scaled values
Boiler count/capacity, turbine capacity, electricity demand level, and battery specs are sized to be internally consistent with the grounded numbers (e.g., boiler capacity comfortably covers total steam demand). These are NOT sourced from a specific real refinery.
Steam demand components
HP/MP/LP demand is built from representative named consumers (CDU, hydrocracker, hydrotreater, tank heating) rather than one anonymous number, to reflect typical refinery steam end-uses. Exact real-plant demand data is proprietary and was not used.
Do not claim
This model should not be presented as calibrated to, or validated against, any specific named refinery. It should also not be directly compared numerically against savings percentages reported in other published studies (e.g., sugar-mill cogeneration papers) — those used different plant scale, currency, and fuel mix.
Tariff bands used
Peak: 18:00-22:00 (+20% of base). Solar/off-peak: 10:00-16:00 (-20% of base). Normal: all other hours (base rate). Matches the national ToD framework structure; exact state/DISCOM windows vary and should be cited as representative.
Next steps
Use Hourly_Profile columns C-H as the input vectors for the MATLAB baseline script and, later, the MILP (intlinprog). Parameters sheet is the single source of truth — update values there only.